Regulator Checklist

|  |  |
| --- | --- |
| Item Serial Number: | Location: |
| Gas Type: |
| Regulator Type (one or two stage): |
| Date of Inspection: | Inspected by: |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| No | Item | Yes | No | Comments |
| 1 | Date Codes and Identified to BSEN ISO 2503 |  |  |  |
| 2 | Regulator marked for the specific gas used |  |  |  |
| 3 | Date/Code stamped on the rear of the regulator |  |  |  |
| 4 | Regulator in date (5 years non-corrosive gas, 2 years corrosive gas) |  |  |  |
| 5 | Pressure gauge glasses undamaged |  |  |  |
| 6 | Max inlet cylinder pressure suitable for cylinder to be used |  |  |  |
| 7 | Pressure adjust screw screws fully in and out and stays fixed to the body of the regulator |  |  |  |
| 8 | Regulator outlet uncontaminated, thread undamaged and free from oils, greases and PTFE tape |  |  |  |
| 9 | Outlet pressure gauge steady |  |  |  |
| 10 | Inlet pressure steady |  |  |  |
| Inspection assessment: Pass/Fail If fail, remove from use immediately and arrange to service/scrap |